## Power Budget
Main Control Board Power Budget
Team 201, Fill-A-Bot. Nikita Bangiyev. Updated October 16, 2026.
Individual subsystem only: one 5V rail, one 9V wall adapter. Built from the class Power Budget Example template (sections A-E). Currents are in mA.
Blue numbers are inputs you can change. Black numbers are formulas.
A. All powered major components (not power sources or regulators)
Component name | Part number | Supply voltage range | Qty | Max current used (mA) | Total current (mA) | Unit | Value type | Source and basis | Source URL
Curiosity Nano: PIC18F57Q43 plus board target circuits | DM164150 (PIC18F57Q43) | 1.8 to 5.5V; 5V used | 1 | 170 | 170 | mA | Derived ceiling | Microchip gives a maximum IDD only at VDD = 3.0V (Table 47-2: 8.2mA at 64MHz HFINTOSC). There is no 5V maximum. Ceiling: the PIC may not dissipate more than 800mW, so its own supply current is at most 800mW / 4.9V = 163.3mA (my PIC pins sink the LED and pull-up currents; they barely source anything). Add the 5.5mA Nano allowance = 168.8mA, rounded up to 170mA. This is not a datasheet operating current. | https://ww1.microchip.com/downloads/aemDocuments/documents/MCU08/ProductDocuments/DataSheets/PIC18F27-47-57Q43-Microcontroller-Data-Sheet-XLP-DS40002147.pdf
Dual op amp, both channels plus feedback load | MCP6002-I/P | 1.8 to 6.0V; 5V used | 1 | 0.856 | 0.856 | mA | Datasheet max + calculated | 2 x 0.170mA IQ max (guaranteed at 25C) + 5.1V / 9.9k ohm = 0.515mA, a bound on the current U3A or U3B can push through Rin and Rf. The +/-30mA supply-pin figure is an absolute-maximum stress rating, not a current the part uses, so it is not used. | https://ww1.microchip.com/downloads/en/DeviceDoc/MCP6001-1R-1U-2-4-1-MHz-Low-Power-Op-Amp-DS20001733L.pdf
LCD logic, including its built-in ST7066U controller | NHD-0216K1Z-FL-YBW | 4.5 to 5.5V; 5V used | 1 | 3 | 3 | mA | Datasheet max | Electrical Characteristics: IDD 3.0mA max at VDD = 5.0V (typ 1.0mA). Counted once. No separate driver IC. | https://newhavendisplay.com/content/specs/NHD-0216K1Z-FL-YBW.pdf
LCD backlight at full brightness | NHD-0216K1Z-FL-YBW | 4.9 to 5.1V; 5V used | 1 | 156 | 156 | mA | Datasheet max | Electrical Characteristics: ILED 156mA max at VLED = 5.0V (typ 130mA), built-in resistor. The rail can reach 5.1V; the 25% margin covers the small extra current. | https://newhavendisplay.com/content/specs/NHD-0216K1Z-FL-YBW.pdf
LDR cup-sensor divider | PDV-P8103 + 10k ohm 1% | 5V used; cell rated 150V | 1 | 0.516 | 0.516 | mA | Calculated bound | 5.1V / 9.9k ohm = 0.515mA even if the LDR went to 0 ohm. The datasheet gives resistance and power, not a supply current. | https://media.digikey.com/pdf/data%20sheets/photonic%20detetectors%20inc%20pdfs/pdv-p8103.pdf
Major-component subtotal |  |  |  |  | 330.372 | mA
Value types: Datasheet max = guaranteed limit from the manufacturer's electrical table. Calculated bound = Ohm's law with the rail at 5.1V and the resistor at its minimum value. Derived ceiling = built from an absolute-maximum rating because no 5V operating maximum is published. Typical values are listed only for comparison and are not used in the totals.
B. 5V rail: every load assigned once, then one 25% safety margin
Component name | Part number | Supply voltage range | Qty | Max current used (mA) | Total current (mA) | Unit | Value type | Source and basis | Source URL
Curiosity Nano: PIC18F57Q43 plus board target circuits | DM164150 (PIC18F57Q43) | 1.8 to 5.5V; 5V used | 1 | 170 | 170 | mA | Derived ceiling | Same as Section A.
Dual op amp, both channels plus feedback load | MCP6002-I/P | 1.8 to 6.0V; 5V used | 1 | 0.856 | 0.856 | mA | Datasheet max + calculated | Same as Section A.
LCD logic, including its built-in ST7066U controller | NHD-0216K1Z-FL-YBW | 4.5 to 5.5V; 5V used | 1 | 3 | 3 | mA | Datasheet max | Same as Section A.
LCD backlight at full brightness | NHD-0216K1Z-FL-YBW | 4.9 to 5.1V; 5V used | 1 | 156 | 156 | mA | Datasheet max | Same as Section A.
LDR cup-sensor divider | PDV-P8103 + 10k ohm 1% | 5V used; cell rated 150V | 1 | 0.516 | 0.516 | mA | Calculated bound | Same as Section A.
LCD E pull-down (while E is high) | 100k ohm | 5V | 1 | 0.052 | 0.052 | mA | Calculated bound | 5.1V / 99k ohm = 0.052mA. Sourced by RC5.
LCD contrast trimmer | 10k ohm trimmer | 5V | 1 | 0.638 | 0.638 | mA | Calculated bound | 5.1V / 8k ohm = 0.638mA.
Three status LED branches | LED + 2.2k ohm each | 5V | 1 | 7.026 | 7.026 | mA | Calculated bound | Each 5.1V / 2.178k ohm = 2.342mA with zero LED drop. Real current is about 1.4mA each.
Four button pull-ups (all pressed) | 10k ohm each | 5V | 1 | 2.061 | 2.061 | mA | Calculated bound | 4 x 5.1V / 9.9k ohm = 2.061mA.
Two host I2C pull-ups (both lines low) | 4.7k ohm each | 5V | 1 | 2.193 | 2.193 | mA | Calculated bound | 2 x 5.1V / 4.653k ohm = 2.193mA. No other board adds pull-ups.
Total 5V load before margin |  |  |  |  | 342.342 | mA
Safety margin |  |  |  |  | 25% |  |  | Class requirement: 25% added once.
Total 5V current required, including margin |  |  |  |  | 427.928 | mA
5V load power including margin (at 5.0V) |  |  |  |  | 2.1396 | W
C. Regulator for the 5V rail
Component name | Part number | Supply voltage range | Qty | Max current used (mA) | Total current (mA) | Unit | Value type | Source and basis | Source URL
5V low-dropout linear regulator | LM1086IT-5.0/NOPB (TO-220) | 6.5 to 20V in for full accuracy; 9V used | 1 | 1500 | 1500 | mA | Datasheet rating | TI SNVS039J: 1.5A output; current limit 1.5A min. This is what it can supply, not what it uses. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Required 5V current including margin |  |  |  |  | 427.928 | mA
Electrical current remaining |  |  |  |  | 1072.072 | mA
Thermal current capability with the heat sink (from thermal check) |  |  |  |  | 1220 | mA
Current remaining before the thermal limit |  |  |  |  | 792.072 | mA
D. External power source
Component name | Part number | AC input range | DC V | Capacity (mA) | Current (mA) | Unit | Value type | Source and basis | Source URL
Regulated 9V wall adapter | Triad Magnetics WSU090-2000 | 90 to 264VAC | 9 | 2000 | 2000 | mA | Datasheet rating | Triad WSU090-2000 spec: 9VDC, 2.0A, +/-5% line and load regulation, 150mV p-p ripple max, 0 to 40C at full load. 5.5 x 2.1 x 11mm plug, center positive. | https://catalog.triadmagnetics.com/Asset/WSU090-2000.pdf
Regulator connected to this source: LM1086 rating (class template method) |  |  |  |  | 1500 | mA
Total remaining on the source, class template method (must not be negative) |  |  |  |  | 500 | mA
Regulator output current including margin |  |  |  |  | 427.928 | mA
Regulator quiescent (ground) current, max |  |  |  |  | 10 | mA | Datasheet max | LM1086-5.0: 10mA max, VIN <= 20V (typ 5mA). Added once, after the margin. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Actual adapter current needed (linear regulator: Iout + Iq) |  |  |  |  | 437.928 | mA
Adapter current remaining, actual load |  |  |  |  | 1562.072 | mA
Adapter DC power used |  |  |  |  | 3.9414 | W
E. Battery life
Battery source |  |  |  |  | N/A |  |  | Wall adapter only. No battery is used.
Battery capacity |  |  |  |  | N/A
Worst-case battery life |  |  |  |  | N/A
Voltage, dropout, and thermal checks (40C enclosure, natural convection)
Supply voltage check
Adapter nominal output voltage |  |  |  |  | 9 | V
Adapter voltage tolerance |  |  |  |  | 5% |  | Datasheet max | Triad: +/-5% line and load regulation. | https://catalog.triadmagnetics.com/Asset/WSU090-2000.pdf
Highest adapter voltage |  |  |  |  | 9.45 | V
Lowest adapter voltage |  |  |  |  | 8.55 | V
Regulator nominal output voltage |  |  |  |  | 5 | V | Datasheet | LM1086-5.0 fixed output. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Lowest regulated output voltage |  |  |  |  | 4.9 | V | Datasheet min | LM1086-5.0: 4.900V min over the full range (VIN 6.5 to 20V, 0 to full load, full temperature). | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Highest regulated output voltage |  |  |  |  | 5.1 | V | Datasheet max | LM1086-5.0: 5.100V max over the same conditions. Matches the LCD backlight's 4.9 to 5.1V range. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Adapter ripple, peak-to-peak |  |  |  |  | 0.15 | V | Datasheet max | Triad: 150mV p-p max. | https://catalog.triadmagnetics.com/Asset/WSU090-2000.pdf
Regulator dropout voltage, max |  |  |  |  | 1.5 | V | Datasheet max | LM1086: 1.5V max at 1.5A over the full range. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Lowest regulator input (low adapter, minus half the ripple, minus cord and jack drop) |  |  |  |  | 8.4084 | V | Calculated
Input needed to stay in regulation (highest output + max dropout) |  |  |  |  | 6.6 | V | Calculated | Also above the 6.5V minimum for the 4.9 to 5.1V accuracy spec.
Dropout headroom |  |  |  |  | 1.8084 | V | Calculated | Must be positive.
Thermal check
Enclosure ambient design temperature |  |  |  |  | 40 | C | Assumption | Design assumption. The adapter is also rated to 40C at full load.
Junction to tab, LM1086 TO-220 (output section, used for both) |  |  |  |  | 4 | C/W | Datasheet | SNVS039J table 6.4: RthetaJC(bot) 1.5 (control) / 4.0 (output) C/W. Using 4.0 is conservative. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Insulating pad and mounting allowance |  |  |  |  | 1 | C/W | Datasheet + allowance | Bergquist SP900S-0.009-00-54 TO-220 pad lists 0.61 C/W. I budget 1 C/W for mounting variation. | https://www.digikey.com/en/products/detail/bergquist/SP900S-0-009-00-54/307797
Heat sink, natural convection |  |  |  |  | 10 | C/W | Datasheet | Same Sky HSE14-384225P: 10.0 C/W at 1W (19.2C rise at 2W = 9.6 C/W). Conservative near 2W. | https://www.sameskydevices.com/product/resource/hse14-384225p.pdf
Total junction-to-ambient resistance |  |  |  |  | 15 | C/W | Calculated
Junction temperature limit used |  |  |  |  | 125 | C | Datasheet max | LM1086 control section TJ max 125C (output section 150C). Using 125C for everything is conservative. | https://www.ti.com/lit/ds/symlink/lm1086.pdf
Allowable regulator dissipation |  |  |  |  | 5.6667 | W | Calculated
Regulator dissipation at the budget load: (Vin high - Vout low) x Iout + Vin high x Iq |  |  |  |  | 2.0416 | W | Calculated
Estimated junction temperature |  |  |  |  | 70.6236 | C | Calculated
Thermal current capability, rounded down to 10mA |  |  |  |  | 1220 | mA | Calculated | Output current that would reach the 125C limit at 40C.
Junction temperature margin |  |  |  |  | 54.3764 | C | Calculated
Heat sink temperature rise |  |  |  |  | 20.4157 | C | Calculated | Keep the sink away from the LCD (rated to 70C).
Notes: (1) The 3.0V PIC IDD table is not a guaranteed maximum at 5.0V, so the 170mA Nano entry is a derived ceiling, not a datasheet operating current. (2) Stress ratings (PIC 350mA VSS pin, MCP6002 +/-30mA) are not used as operating currents. (3) The LCD values are specified at 5.0V and 25C. (4) Real current, plug fit, cup detection, and enclosure temperature still need prototype measurements.
Inputs used by the formulas above
Input |  |  |  |  | Value | Unit | Value type | Source and basis | Source URL
PIC absolute-maximum total power dissipation |  |  |  |  | 800 | mW | Absolute max (stress) | DS40002147H, section 47.1 Absolute Maximum Ratings: total power dissipation 800mW. Used only to build a ceiling, never as an operating point. | https://ww1.microchip.com/downloads/aemDocuments/documents/MCU08/ProductDocuments/DataSheets/PIC18F27-47-57Q43-Microcontroller-Data-Sheet-XLP-DS40002147.pdf
Nano board target-side allowance |  |  |  |  | 5.5 | mA | Engineering allowance | LED0 (yellow LED with 1k ohm to VCC_TARGET, schematic R202/D200): 5.1V / 950 ohm = 5.37mA with zero LED drop and a -5% resistor. Level shifters and voltage monitor: about 0.1mA (user guide 3.3.2). Sum 5.47mA, rounded up to 5.5mA. | https://ww1.microchip.com/downloads/aemDocuments/documents/MCU08/ProductDocuments/UserGuides/PIC18F57Q43-Curiosity-Nano-HW-UserGuide-DS40002186B.pdf
MCP6002 quiescent current per amplifier, max |  |  |  |  | 0.17 | mA | Datasheet max | DS20001733L DC table: IQ 170uA max per amplifier, IO = 0, VDD = 5.5V, TA = +25C. | https://ww1.microchip.com/downloads/en/DeviceDoc/MCP6001-1R-1U-2-4-1-MHz-Low-Power-Op-Amp-DS20001733L.pdf
Amplifiers in the MCP6002 package |  |  |  |  | 2 | # | Count | Dual op amp: U3A buffer and U3B gain stage.
Divider, button, and Rin resistor value |  |  |  |  | 10000 | ohm | Selected value | LDR divider R1, four button pull-ups, and U3B Rin are all 10k ohm, 1%.
Fixed resistor tolerance |  |  |  |  | 0.01 |  | Selected value | 1% resistors. Minimum resistance = value x (1 - tolerance).
Contrast trimmer resistance |  |  |  |  | 10000 | ohm | Selected value | 10k ohm trimmer from 5V to GND, wiper to LCD V0.
Contrast trimmer tolerance |  |  |  |  | 0.2 |  | Assumption | Conservative +/-20% trimmer tolerance.
Status LED series resistor |  |  |  |  | 2200 | ohm | Selected value | 2.2k ohm, 1%, one per LED. Zero LED forward drop assumed for a worst-case bound.
Number of status LEDs |  |  |  |  | 3 | # | Count | Dispensing, Done, Fault.
Number of buttons with pull-ups |  |  |  |  | 4 | # | Count | UP, DOWN, START, STOP. Worst case: all pressed.
I2C pull-up resistor |  |  |  |  | 4700 | ohm | Selected value | One 4.7k ohm pull-up each on SDA and SCL, host board only. Worst case: both lines held low.
Number of I2C pull-ups |  |  |  |  | 2 | # | Count | SDA and SCL.
LCD E pull-down resistor |  |  |  |  | 100000 | ohm | Selected value | 100k ohm from E to GND. Draws current only while RC5 drives E high.
Adapter cord and jack resistance, round trip |  |  |  |  | 0.152 | ohm | Calculated estimate | 20 AWG, 6 ft cord: 2 x 1.83m x 33.3 mohm/m = 0.122 ohm, plus 0.030 ohm jack contact (PJ-102AH datasheet). Used only for the dropout check. | https://www.sameskydevices.com/product/resource/pj-102ah.pdf